EMERGENCY & EXIT LIGHTING                    EL – 3

INSPECTION & SERVICE: 6 MONTHS

| NOTE: |  |
| --- | --- |
|  | JHA Required Qualified Person Manual (EL-2) |

Assigned:

Date Assigned:

Date Completed:

INSTRUCTIONS

Perform the following prior to competent fire practitioner performing service (If applicable)

- Check for normal operation of exit and emergency lights. Verify charge light indicating

- Press test button to ensure light switches to emergency mode

- Change any tubes or globes not functioning (as applicable)

- Verify exit signage is correct as per posted evacuation sign/diagram

- Operate emergency button (if fitted) or isolate supply by turning off associated breakers for test

- Clean lights and diffusers with supply off and isolated

- Ensure lights operate off battery supply for 90 minutes

- Note any failed fittings for battery or fitting replacement

- Re-energise circuit and check for normal operation of lights

Needed Repairs or Additional Comments