EXTERIOR LIGHTING                                     EL – 7

INSPECTION & SERVICE: 12 MONTHS

| NOTE: |  |
| --- | --- |
|  | HIGH RISK JHA Required Qualified Person |

Assigned:

Date Assigned:

Date Completed:

INSTRUCTIONS

Check all exterior lights at facility for correct operation.  Note any lights that do not function correctly.

PARKING LOTS/EAVES

- Ensure power is isolated

- Check for damaged fixtures

- Check light poles for rust or corrosion and treat as required. Check fasteners for tightness

- Remove tree branches or obstacles in front of each fixture

- Clean exterior of fittings. Remove diffusers and clean internally with duster or cloth

- Replace burnt out bulbs using the same style and wattage bulb

LIGHT OPERATION / CONTROL

After servicing all lights, turn all lights on to verify operation, by performing the following:

- Clean photocells with glass cleaner and dry with a paper towel

- Check operation of Photoelectric (PE) cell / daylight switch by covering with test cap

- Check operation of timers

Needed Repairs or Additional Comments