SWITCHBOARD                  		  		       EL – 2

INSPECTION & SERVICE: 4 YEARS

| NOTE: |  |
| --- | --- |
|  | HIGH RISK JHA Required Qualified Person Manual (EL-1) |

Assigned:

Date Assigned:

Date Completed:

INSTRUCTIONS

Perform a thorough clean and service on all main, meter and distribution boards.

SWITCHBOARD EXTERNAL

- Ensure sufficient clearance maintained in front of panels for access

- Clear all items from switch-room (If applicable)

- Check frame and covers are mechanically in good condition

- Check switchboard for rust spots. Treat any rust as required

- Check connection of earth cable to earth stake. Remove corrosion if identified

- Measure earth resistance and record

SWITCHBOARD INTERNAL

- Confirm panels and circuits are correctly labeled

- Inspect cabling and insulation for discoloration at connection points

- Inspection condition of seals and penetrations

- Check escutcheon panel and switchboard doors close firmly and seal correctly

- Confirm that pole fillers are in place to cover empty spaces

- Vacuum clean interior with an all rubber or all plastic hose

- Verify all circuit breakers and equipment are mechanically and electrically in good condition

- Check and tighten all cable terminations

- Check only one cable is installed in each Neutral or Earth terminal

- Reinstate distribution board supply only when all persons are clear from panel

Needed Repairs or Additional Comments