COMPLIANCES		                       	      		B – 18

INSPECTION: MONTHLY

| NOTE: |  |
| --- | --- |
|  | To be used by facilities in New Zealand ONLY |

Assigned:

Date Assigned:

Date Completed:

INSTRUCTIONS

This Job Card may be carried out by a Competent/Trained person, which verifies required and scheduled Compliance Inspections have taken place.

These checks and inspections are directly linked to the building’s “Compliance Schedule.” Routine checks are required to ensure that the building can be legally occupied and that an annual Building Warrant of Fitness (BWOF) may be obtained.

Perform the following:

- Check to see that all scheduled inspections, including Independent Qualified Person (IQP) inspections, have been made

- Ensure specified systems have been checked to the required frequency and procedure

- Ensure date, issues and/or comments have been recorded in Compliance Logbook

- Report any inspections not completed to person of Oversight

- Ensure that IQP’s are instructed to perform the annual inspections and issue the BWOF

The following is an outline of the required inspections and checks:

(SS2) AUTOMATIC OR MANUAL EMERGENCY WARNING SYSTEMS

- The fire alarm system shall be inspected and tested monthly by activating the ‘evacuation’ function on the alarm control panel and annually to NZS 4512 by an IQP.  All tests shall be recorded on the SS2 form contained in the Compliance Log Book.

(SS4) ILLUMINATED EXITS LIGHTS / EMERGENCY LIGHTING SYSTEMS

- Emergency lighting systems shall be inspected and checked monthly as set out in the task instructions by a competent person and annually by an IQP. All tests shall be recorded on the SS4 form, contained in the Compliance Log Book.

(Continued)

INSTRUCTIONS

(SS15/2) FINAL EXITS

- Final exits shall be inspected monthly by a competent person and annually by an IQP.  Inspections shall be made to ensure that final exits perform as designed for safe evacuation, and in particular that:

- Final exits are kept clear of obstacles and hazards

- Final exit doors are not locked, barred, or blocked so as to prevent occupants from leaving the building in the event of an emergency without the use of a key

- All tests shall be recorded on the SS15/2 form contained in the Compliance Log Book.

Needed Repairs or Additional Comments